## Slide 1
We Shouldn’t have Been Surprised
Almost 15 years ago I had a conversation with a government representative regarding the oxygen supply and a Pandemic.
We discussed the limitations of the bulk oxygen system

## Slide 2: Weak Links in the Chain
Primary supply
  Once a monthly delivery is optimal and most major gas suppliers try to design for this size.
  LOX trailers are limited to ͌ 6000 gal. (͌ 690,000 scf)
The primary supply is not usually the weakest link in the chain.

## Slide 3: Weak Links in the Chain
Reserve Supply
  Code requires alarming at “one average days supply”
  This alarm setpoint needs to take into account
    Tank heal (Unusable product)
    Saturated gas. ͌ 96 scf/gal vs. ͌ 115 scf/gal
  Most suppliers require 72 hours
The reserve supply is also not usually the weakest link in the chain.

## Slide 4: Weak Links in the Chain
System regulators
  Typical 1” Generant/Rego ͌ 17,000 scfh in oxygen service
  Diaphragms and seats are rated for -40°F to +165°F.
  High flow applications XXXXX pilot operated regulators are used.
While regulators can be a wink link they are not the weakest link in the chain.

## Slide 5: Weak Links in the Chain
Vaporizers
  The problem child
  Industry rating is at 70°F / 8 hours / 70%RH
  At rated capacity output is 20°F below ambient
  Capacities decrease:
    With extended run time
    Lack of air circulation
    Lack of sun exposure

## Slide 6: Weak Links in the Chain
Vaporizers
  Proper sizing is critical
  While there are sizing programs it is the old adage, “Garbage in garbage out”
  Use rates typically based on historical usage, with some adders.
The vaporizers are the weakest link in the chain.

## Slide 7: Short Term Solution
Increase air circulation

## Slide 8: Short Term Solution
Deice the vaporizer
NOT LIKE THIS!!!!!

## Slide 9: Long Term Solution
Resize based on the lessons learned.
Consider Switching
  Allows a vaporizer to defrost
  Easier to defrost heavily iced vaporizer
Air Circulation
  Allows a vaporizer to defrost
Consider Powered Vaporizers

## Slide 10: Think Before you Act!

## Slide 11: CGA Standards for COVID-19 Response
The following CGA publications provide guidance on topics related to the industry’s response to the novel Coronavirus (COVID-19) pandemic.
CGA P-83, Guidelines for Cleaning Externally Contaminated Medical Gas Containers
CGA SA-35, Safety Alert, Cleaning of Cylinders Returned from Healthcare Facilities During a Pandemic
CGA C-10, Guideline to Prepare Cylinders and Tubes for Gas Service and Changes in Gas Service
CGA M-18, Standard for the Change of Product and Change of Grade for High Pressure and Refrigerated Liquid Containers
CGA SA-36, Safety Alert, Cylinder and Cryogenic Container Issue Related to Cylinder Conversion and Filling During the COVID-19 Crisis (1st ed)
CGA SA-37, Safety Alert, Medical Oxygen Supply System Issues During the COVID-19 Crisis (1st ed)